### Environmental Products Part 2 of 2
V1.4—14 May 1999
Systems and Options Catalog

Prestige Series 3000/6000 Office/Data Center Models

Powerware Profile Office/Data Center Models

Powerware Plus Office/Data Center Models

One UPS Plus Desktop Models

UPS Options

Modular Power Distribution/Conditioning Systems

Transient Voltage Surge Suppressers (TVSS)

Compaq and the names of Compaq products referenced herein are either trademarks and/or service marks or registered trademarks and/or service marks of Compaq.

DIGITAL is a Trademark of Compaq Computer Corporation.

Microsoft, Windows, Windows NT, SQL Server, Office and BackOffice are either trademarks or registered trademarks of Microsoft Corporation.

Intel and Pentium are registered trademarks of Intel Corporation.

Other product and company names mentioned herein may be trademarks and/or service marks of their respective owners.

### Prestige Series 3000/6000 Office/Data Center Models

The Powerware Prestige 3000 (2.5 kVA and 3 kVA ) and 6000 (4.5 kVA and 6 kVA) UPS are the first on-line UPS that offer a hot-swappable modular design. The Prestige 6000 is easily upgradable from 4.5 kVA to 6 kVA.

The standard North American unit consists of three plug and play modules which can be easily diagnosed and swapped out or upgraded by the user.

The electronics module contains automatic bypass and communications port.

The battery module can be monitored through the software for the Prestige 3000 and Prestige 6000.

The PowerPass maintenance bypass module allows the electronics to be safely disconnected without interrupting the critical load.

The standard international version comes with or without the PowerPass module.

The Prestige North American unit is available in 208 V or 240 V input and 120, 120/208, 120/240 VAC output models.  A 120VAC input/output 3 kVA model is also available. The International unit is switch selectable for 200/208/220/230/240 volts in and out.

Double-conversation on-line technology provides regenerated, clean power at all times for consistent performance.

The user-friendly front panel features visual and audible alarms for battery, overload and change of state, LED bar graph display of percent load, battery time remaining and operational status. The unit also provides an automatic battery self-test feature. Optional network power management and UPS monitoring/shutdown software and network adapters allow safe shutdown, remote status display and control of UPS parameters in an NMS or SNMP environment.

The on-line design extends battery life and the cell saver utility interface gives the Powerware Prestige the ability to accept lower input voltages when the UPS load is at less than 100% capacity.  The battery is used only during the most severe brownouts and blackouts, running cooler and increasing battery life.

The modular battery packs of the Prestige models can be changed, added or removed without turning off the UPS.  This provides regulated on-line power while the battery is being serviced or upgraded.

The PowerPass Distribution Module houses an isolation transformer to provide galvanic isolation to the load during normal operation or while on auto or maintenance bypass. It also contains the output receptacles and ensures high availability by allowing the critical load to be manually transferred to the utility power source (bypass) without interruption.  Extra output receptacles are provided by extendible plug-in distribution modules.  Each receptacle on the extendible module has individual circuit breaker protection for maximum flexibility.  For added flexibility, optional mobile module stackers are available to consolidate and mobilize Prestige Series 3000 and 6000 modules.  Stacker units include seismic mounting provisions.

The Prestige is manufactured by Exide Electronics in accordance with ISO9001 standards for quality throughout the design, documentation, and manufacturing processes. All models are compatible with Power Management software that ships with AlphaServers and includes a 3 year next day advance exchange warranty.   Cable kit or Network adapter is required to communicate with software.  Consult software section for detail.

Step 1—Packaged Systems

Packaged systems include PowerPass output module unless otherwise noted.

Rackmount kit (part number 4N-AEAEO-RC) is available for any Prestige 3000.

Prestige 3000 Series Models

|  | Voltage selections |
| --- | --- |
|  | Input | Output | Input Plug | Output Rating | Output Receptacles |
| 4N-AEAAH-EA1 | 120V | 120V | L5-30P | 3 kVA/2 kW, 60Hz | (1)L5-30R, (1)5-15R |
| 4N-AEAAH-AL | 208V | 120/208V | L6-30P | 3 kVA/2 kW, 60Hz | (1)L6-30R, (4)5-15R |
| 4N-AEAAH-AM | 208V | 120V | L6-30P | 3 kVA/2 kW, 60Hz | (1)L5-30R, (4)5-15R |
| 4N-AEAAH-AN | 240V | 120/240V | L6-30P | 3 kVA/2 kW, 60Hz | (1)L14-30R, (4)5-15R |
| 4N-AEAAH-AP | 240V | 120V | L6-30P | 3 kVA/2 kW, 60Hz | (1)L5-30R, (4)5-15R |
| 4N-AEAAH-AR 1 | 200/240V | 200/240V | VDE pigtail | 3 kVA/2 kW, 50/60Hz | (1)IEC 320 16A |
| 4N-AEAAH-AS | 200/240V | 200/240V | VDE pigtail | 3 kVA/2 kW, 50Hz | (3)IEC320, 10A, (1)IEC320 16A |
| 4N-AEAAH-AT | 240V | 120/240V | L6-30P | 3 kVA/2 kW, 60Hz | (1)L6-30R, (4)5-15R |
| 4N-AEABG-BG1 | 200/240V | 120/240V | VDE pigtail | 2.5 kVA/1.6 kW, 50Hz | (3)IEC320, 10A, (1)IEC320 16A |

### Prestige Series 3000/6000 Office/Data Center Models (continued)

Prestige 6000 Series Models (4.5 kVA)

|  | Voltage selections |
| --- | --- |
|  | Input | Output | Input Plug | Output Rating | Output Receptacles |
| 4N-AEAAJ-AL | 208V | 120/208V | L6-30P | 4.5 kVA/3 kW, 60Hz | (2)L6-30R, (8)5-15R |
| 4N-AEAAJ-AM | 208V | 120V | L6-30P | 4.5 kVA/3 kW, 60Hz | (2)L5-30R, (8)5-15R |
| 4N-AEAAJ-AN | 240V | 120/240V | L6-30P | 4.5 kVA/3 kW, 60Hz | (2)L14-30R, (8)5-15R |
| 4N-AEAAJ-AP | 240V | 120V | L6-30P | 4.5 kVA/3 kW, 60Hz | (2)L5-30R, (8)5-15R |
| 4N-AEAAJ-AK1 | 200/240V | 200/240V | Hardwired | 4.5 kVA/3 kW, 50/60Hz | Hardwired |

Prestige 6000 Series Models (6 kVA Models)

| 4N-AEAAJ-CK1 | 208/240V | 208/240V | Hardwired | 6 kVA/4 kW, 50/60Hz | Hardwired |
| --- | --- | --- | --- | --- | --- |
| 4N-AEAAJ-CL | 208V | 120/208V | L6-30P | 6 kVA/4 kW, 60HZ | (2)L6-30R, (8)5-15R |
| 4N-AEAAJ-CM | 208V | 120V | L6-30P | 6 kVA/4 kW, 60HZ | (2)L5-30R, (8)5-15R |
| 4N-AEAAJ-CN | 240V | 120/240V | L6-30P | 6 kVA/4 kW, 60HZ | (2)L14-30R, (8)5-15R |
| 4N-AEAAJ-CP | 240V | 120V | L6-30P | 6 kVA/4 kW, 60HZ | (2)L5-30R, (8)5-15R |
| 4N-AEAAJ-CR | 240V | 120/240V | L6-30P | 6 kVA/4 kW, 60HZ | (2)L6-20R, (8)5-15R |
| 4N-AEAAJ-CS | 208V | 120/208V | L6-30P | 6 kVA/4 kW, 60HZ | (2)L6-20R, (8)5-15R |
| 4N-AEAAJ-CT | 240V | 120/240V | L6-30P | 6 kVA/4 kW, 60HZ | (2)L6-30R, (8)5-15R |
| 4N-AEAAJ-CU | 200-240V | 200-240V | Hardwired | 6 kVA/4 kW, 50HZ | Hardwired with PowerPass |

1.	Packaged systems noted do not require, and do not include the PowerPass module.

Step 1a—Custom Building Blocks

Select UPS and add optional PowerPass module from step 1b as required.  Custom building block models do not include PowerPass module.

Prestige 6000 Series Models

| 4N-AEAAJ-AJ | 208V/240V | 208V/240V | L6-30P | 4.5 kVA/3 kW, 50/60 Hz | (1)L6-30R |
| --- | --- | --- | --- | --- | --- |
| 4N-AEAAJ-CJ | 208V/240V | 208V/240V | L6-30P | 6 kVA/4 kW, 50/60 Hz | (1)L6-30R |

Step 1b—PowerPass Modules (Optional)

Plugs into L6-30R on UPS Electronics Cabinet; 60 Hz applications only (Optional)

Note:	For hardwired I/O applications, use the hardwired I/O PowerPass module listed below to preserve hot-swap maintenance bypass capability.

Prestige 6000 Series PowerPass Modules

| 4N-AEAAJ-DA | PowerPass 208V Model | 208V | 120V | L6-30P | (2)L5-30R, (4)5-15R2 |
| --- | --- | --- | --- | --- | --- |
| 4N-AEAAJ-DB | PowerPass 208V Model | 208V | 120/208V | L6-30P | (2)L6-20R, (4) 5-15R2 |
| 4N-AEAAJ-DC | PowerPass 208V Model | 208V | 120/208V | L6-30P | (2)L6-30R, (4) 5-15R2 |
| 4N-AEAAJ-DD | PowerPass 208V Model | 208V | 120/240V | L6-30P | (2)L14-30R, (4) 5-15R2 |
| 4N-AEAAJ-DE | PowerPass 240V Model | 240V | 120V | L6-30P | (2)L5-30R, (4) 5-15R2 |
| 4N-AEAAJ-DF | PowerPass 240V Model | 240V | 200/240V | L6-30P | (2)L6-20R, (4) 5-15R2 |
| 4N-AEAAJ-DG | PowerPass 240V Model | 240V | 200/240V | L6-30P | (2)L6-30R, (4) 5-15R2 |
| 4N-AEAAJ-DH | PowerPass 240V Model | 240V | 120/240V | L6-30P | (2)L14-30R, (4) 5-15R2 |
| 4N-AEAAJ-DJ | PowerPass 208V Model | 208V | 120/208V | Hardwired | Hardwired I/O |
| 4N-AEAAJ-DK | PowerPass 240V Model | 240V | 120/240V | Hardwired | Hardwired I/O |
| 4N-AEAAJ-DL | PowerPass 240V Model | 240V | 240V | Hardwired | Hardwired I/O |

### Prestige Series 3000/6000 Office/Data Center Models (continued)

Step 2—Additional Power Distribution Units (Optional)

Plug-In Outlet Extensions plug into receptacle on PowerPass module.  All extensions apply to any UPS listed in the applicable group.

| Extension Models | Includes Output Receptacles | Used with UPS Model1 | Extension plug type |
| --- | --- | --- | --- |
| 4N-AEACH-AK 4N-AEACH-AL | Two L6-20R and two L6-30R Hardwired output module (3 kVA models only) | 4N-AEAAH-AL 4N-AEAAH-AT 4N-AEAAJ-CL 4N-AEAAJ-AL | L6-30P (all) |
| 4N-AEACH-AA 4N-AEACH-AB 4N-AEACH-AC 4N-AEACH-AD 4N-AEACH-AF 4N-AEACH-AE | Four 5-15R2 Four 5-20R2 Two L5-30R and Two 5-20R2 Two L5-20R, Two 5-20R2 One 5-15R2, Three L5-30R Hardwired output module (3 kVA models only) | 4N-AEAAH-AM 4N-AEAAH-AP 4N-AEAAH-EA 4N-AEAAJ-AM 4N-AEAAJ-CM | L5-30P (all) |
| 4N-AEACH-AG 4N-AEACH-AH 4N-AEACH-AJ 4N-AEACH-AM | One L14-30R and three 5-15R2 One L14-30R, Two L6-30R, and One 5-15R2 Hardwired output module (3 kVA models only) Four 5-15R2 | 4N-AEAAH-AN 4N-AEAAJ-AN 4N-AEAAJ-CN | L14-30P (all) |
| 4N-AEACH-DA2 4N-AEACH-DB2 4N-AEACH-DC2 | Schuko outlets six @ 16 Amps French outlets six @ 16 Amps British outlets six @ 13 Amps | 4N-AEAAH-AR 4N-AEAAH-AS | IEC320 C19 16A(all) |

1.	Extensions may also be used with any building block PowerPass module 4N-AEAAJ-D* having the corresponding mating receptacle.

2.	For 3 kVA models only: call for the plug connections available for 4.5 or 6 kVA models.

Step 3—Battery Cabinets for Additional Battery Packs (Optional)

| 4N-AEAAH-AB | Battery Cabinet for 3 kVA Models (up to 3 total maximum recommended)3 |
| --- | --- |
| 4N-AEAAJ-CC | Battery Cabinet for 4.5 and 6 kVA Models (up to 6 total maximum recommended)3 |

3.	Limitations are to minimize battery recharge time.

Battery Support Times (in Additional Cabinets)

STD equals one battery for 3 kVA; two batteries for 4.5, and two batteries for 6 kVA models.

| Battery Times | STD | STD+1 | STD+2 | STD+3 | STD+4 |
| --- | --- | --- | --- | --- | --- |
| 3 kVA @ full load 3 kVA @ half load | 7 minutes 14 minutes | 18 minutes 35 minutes | 30 minutes 55 minutes | N/A | N/A |
| 4.5 kVA @ full load 4.5 kVA @ half load | 12 minutes 30 minutes | 20 minutes 50 minutes | 28 minutes 68 minutes | 36 minutes 90 minutes | 44 minutes 116 minutes |
| 6 kVA @ full load 6 kVA @ half load | 8 minutes 20 minutes | 12 minutes 33 minutes | 18 minutes 44 minutes | 24 minutes 56 minutes | 30 minutes 74 minutes |

Step 4—UPS Monitoring/Shutdown Software and Network Connectivity Adapter Options

See UPS Software and Options section.

### Prestige Series 3000/6000 Office/Data Center Models (continued)

Step 5—Mobile Module Stack-UPS to consolidate Series 3000/6000 Modules (Optional)

Stack-UPS provides the option of housing the UPS system and providing a method for seismic mounting.  Determine unit requirement from following chart; each unit equals 5.6-inches.

Note:	Batteries may be separated from other modules and housed in separate stacking unit.

|  | Package Contents | Total Units Required |
| --- | --- | --- |
|  | Electronics Module | PowerPass Module | Battery Module | w/PowerPass | w/o PowerPass |
| Series 3000 | 1 unit | 1 unit | 1 unit | 3 units | 2 units |
| Series 6000 | 2 units | 2 units | 2 units | 6 units | 4 units |
| Add-on Battery | N/A | N/A | 1 unit each | add as required |

Step 5a—Select Stack-UPS to match total unit requirement

| 4N-AEACH-HA | Stack-UPS cabinet kit for Powerware Prestige Series UPS (Accommodates up to three units space) |
| --- | --- |
| 4N-AEACH-HB | Stack-UPS cabinet kit for Powerware Prestige Series UPS (Accommodates up to three units space) |
| 4N-AEACH-HC | Stack-UPS cabinet kit for Powerware Prestige Series UPS (Accommodates up to three units space) |
| 4N-AEACH-HD | Stack-UPS cabinet kit for Powerware Prestige Series UPS (Accommodates up to three units space) |

Step 6—Warranty Upgrades1 (Optional)

| 4N-AEWAR-G2/G3 | Prestige 3000/6000 5-year on-site exchange warranty upgrade option upgrades 3-year hot-swap return product warranty for continental US only and is available at time of UPS sale. |
| --- | --- |
| 4N-AEWAR-G4 | Same as above for Prestige 6000 only, except for 5-year on-site and start-up package. |

1.	Service provided by UPS vendor.

Prestige Series 3000 Models Specifications

| Power Requirements | North American Models - 60Hz | International Models - 50Hz |
| --- | --- | --- |
| Input Voltage | 208V or 240 VAC | 200V, 208V, 220V, 230V, 240 VAC |
| Allowable Input Range without using batteries | 160-276 VAC @ full load 140-276 VAC @ half load | 160-276 VAC @ full load 140-276 VAC @ half load |
| Input Frequency | 45 Hz to 65 Hz | 45 Hz to 65 Hz |
| Input Power Factor | 0.90 typical @ full load and nominal line | 0.90 typical @ full load and nominal line |
| Surge Protection | Per EN 50082-1, meets IEC 801-4, IEEE 587, ANSI C62.41 CAT A&B | Per EN 50082-1, meets IEC 801-4, IEEE 587, ANSI C62.41 CAT A&B |
| Input Connection (6’ detachable line cord) (requires 30A-2P circuit)/30A-1P (120V) | With L6-30P (208, 240V) L5-30P (120V) | Stripped Pigtail |
| Output Receptacles (Model Dependent) | (1) L5-30R, (4) 5-15R; | (1) IEC320, 16A |
| Output Receptacles (Options Available) | (1) L6-30R, (4) 5-15R or (1) L14-30R (4) 5-15R, (1) L6-20R, (4) 5-15R | Ext. strip option or (3) IEC320 with PowerPass |
| Output Voltage (Options Available) | 120V, 120/208V, 120/240V±3% (60Hz) | 200V, 208V, 220V, 230V, 240 VAC ± 3% |
| Output VA/Watts | 3000VA/2000W @ 60Hz | 3000VA/2100W @ 50Hz |
| Output Current @ full load | 25A/120V, 14.4A/208V, 12.5A/240V | 14.4A/208V, 13.6A/220V, 13.0A/230V, 12.5A/240V |
| Output Voltage THD/Crest Factor | <5%, 100% non-linear load/3:1 CF | <5%, 100% non-linear load/3:1 CF |
| Normal/Common Mode Noise Rejection @ 100 KHZ | >80 dB/60 dB | >80 dB/60 dB |
| Output Frequency | Same as input, 50 or 60Hz ±0.1% free running ±5% synchronized (adjustable to ±1.5%) | Same as input, 50 or 60Hz ±0.1% free running ±5% synchronized (adjustable to ±1.5%) |
| Battery-sealed lead acid Support time full/half load Recharge time to 90% capacity | 7 min/14 min 6 hrs | 7 min/14 min 6 hrs |

### Prestige Series 3000/6000 Office/Data Center Models (continued)

| Physical Characteristics |
| --- |
| Weight (Battery) | 52 lbs/23.6 kg | 52 lbs/23.6 kg |
| Weight (PowerPass) | 47 lbs/21.4 kg | 47 lbs/21.4 kg |
| Weight (Electronics Module) | 16.5lbs/7.5kg | 16.5lbs/7.5kg |
| Dimensions (Electronics OR Battery OR PowerPass module ) Hx Wx D | 5.6 in x 9.9 in x 15.8 in 143 mm x 252 mm x 400 mm | 5.6 in x 9.9 in x 15.8 in 143 mm x 252 mm x 400 mm |
| Dimensions (Electronics,std battery & PowerPass stacked Hx W x D | 16.8 in x 9.9 in x 15.8 in 429 mm x 252 mm x 400 mm | 16.8 in x 9.9 in x 15.8 in 429 mm x 252 mm x 400 mm |
| Environmental |
| Audible Noise @ 1 meter | 50dBA | 50dBA |
| Operating/Storage Ambient Temperature & Altitude | +10 C to +40 C/-20 C to +60 C; 0-4000 ft (1200 m) without derating | +10 C to +40 C/-20 C to +60 C; 0-4000 ft (1200 m) without derating |
| BTU/Hr (On Line) @ Full Load | 1492 (with PowerPass) | 978 (without PowerPass) |
| Relative Humidity | 5-95% Non-condensing | 5-95% Non-condensing |
| EMI Suppression | FCC Part 15, Subpart J, Class A also meet CISPR22B | FCC Part 15, Subpart J, Class A also meet CISPR22B |
| Safety | UL 1778, CSA | EN 50091-1 |
| Power Requirements | North American Models—60Hz | International Models—50Hz |
| Input Voltage | 208V or 240 VAC | 200V, 208V, 220V, 230V, 240 VAC |
| Allowable Input Range without using batteries | 160-276 VAC @ full load 140-276 VAC @ half load | 160-276 VAC @ full load 140-276 VAC @ half load |
| Input Frequency | 45 Hz to 65 Hz | 45 Hz to 65 Hz |
| Input Power Factor | 0.90 typical @ full load and nominal line | 0.90 typical @ full load and nominal line |
| Surge Protection | Per EN 50082-1, meets IEC 801-4, IEEE 587, ANSI C62.41 CAT A&B | Per EN 50082-1, meets IEC 801-4, IEEE 587, ANSI C62.41 CAT A&B |
| Input Connection (6’ detachable line cord) requires 30A-2P circuit | With L6-30P | Hardwired |
| Output Receptacles (Standard Package) | (2) L5-30R, (8) 5-15R (2) L6-30R, (8 )5-15R | Hardwired |
| Output Receptacles (Options Available) | (2) L6-20R, (8) 5-15R or (2) L14-30R, (8) 5-15R | Call for availability |
| Output Voltage (Options Available) | 120V, 120V/240V, 120V/208 VAC ±3% | 200V, 208V, 220V, 230V, 240 VAC ± 3% |
| Output VA/Watts | 4500VA Model: 37.5/21.6/18.7A 6000VA Model: 50/28.8/25A @ 120V/208V/240V | 4500VA Model: 37.5/21.6/18.7A 6000VA Model: 50/28.8/25A @ 120V/208V/240V |
| Output Current @ full load | 4500VA Model: 37.5/21.6/18.7A 6000VA Model: 50/28.8/25A @ 120V/208V/240V | 4500VA Model: 37.5/21.6/18.7A 6000VA Model: 50/28.8/25A @ 120V/208V/240V |
| Output Voltage THD/Crest Factor | <5%, 100% non-linear load/3:1 CF | <5%, 100% non-linear load/3:1 CF |
| Normal/Common Mode Noise Rejection | >80 dB/60 dB | >80 dB/60 dB |
| Output Frequency | Same as input, 50 or 60Hz ±0.1% free running ±5% synchronized (adjustable to ±1.5%) with PowerPass | Same as input, 50 or 60Hz ±0.1% free running ±5% synchronized (adjustable to ±1.5%) with PowerPass |
| Battery-sealed lead acid Support time full/half load Recharge time to 90% capacity | 8 min/20 min (Model 6000VA); 12 min/30 min (Model 4500VA) 6 hours | 8 min/20 min (Model 6000VA); 12 min/30 min (Model 4500VA) 6 hours |
| Physical Characteristics |
| Weight (Battery) | 52 lbs/23.6 kg | 52 lbs/23.6 kg |
| Weight (PowerPass) | 75 lbs/34.1 kg 60Hz | 75 lbs/34.1 kg 50 Hz |
| Weight (Electronics Module) | 39 lbs/7.82 kg | 39 lbs/7.82 kg |
| Dimensions (each Battery –1 of 2 modules) H x D x W | 5.6 in x 9.9 in x 15.8 in 143 mm x 252 mm x 400 mm each | 5.6 in x 9.9 in x 15.8 in 143 mm x 252 mm x 400 mm each |
| Dimensions (Electronics OR PowerPass module)- PowerPass is model dependent | 11.2 in x 9.9 in x 15.8 in 286 mm x 252 mm x 400 mm | 11.2 in x 9.9 in x 15.8 in 286 mm x 252 mm x 400 mm |
| (Electronics, Powerpass & Batteries stacked) | 33.6in x 9.9 in x 15.8 in | 33.6in x 9.9 in x 15.8 in |

### Prestige Series 3000/6000 Office/Data Center Models (continued)

| Environmental |
| --- |
| Audible Noise @ 1 meter | 50dBA | 50dBA |
| Operating/Storage Ambient Temperature & Altitude | +10 C to +40 C/-20 C to +60 C; 0-4000 ft (1200 m) without derating | +10 C to +40 C/-20 C to +60 C; 0-4000 ft (1200 m) without derating |
| BTU/Hr (On Line) @ Full Load 6000VA Model: 4500VA Model: | 2400 (with PowePass) 2000 (with PowerPass) | 1600 (without PowerPass) 1200 (without PowerPass) |
| Relative Humidity | 5-95% Non-condensing | 5-95% Non-condensing |
| EMI Suppression | FCC Part 15, Subpart J, Class A also meet CISPR22B | FCC Part 15, Subpart J, Class A also meet CISPR22B |
| Safety (includes remote emergency off) | UL 1778, CSA | EN 50091-1 |

### Powerware Profile Office/Data Center Models

The Profile UPS systems are available in three ratings: 
8 kVA/10 kVA/12.5 kVA models to support single-phase loads. The Powerware Profile is a double conversion online UPS for the protection of commercial and technical computer systems and other intelligent devices such as measurement instruments and industrial automation applications.  The standard model features advanced serviceability modular design with internal battery.  The Powerware Profile offers you extended battery time with additional matching cabinets.  A single matching battery cabinet will provide over 1 hour of run time.  Up to 8 hours can be achieved using additional battery cabinets.

In addition to the traditional online operation mode, Powerware Profile features the efficiency optimizer function.  It minimizes the power loss, reduces power consumption and cuts power bills.  The UPS automatically switches between by-pass and online according to the utility power condition.  The efficient optimizer function is standard in all Powerware profile UPS and can be easily be activated.

The Powerware Profile is suitable for both office and computer room environments.  All models are voltage and frequency selectable for 200-240V, 50 Hz or 60 Hz outputs and feature a wide input tolerance of 170-292V without using battery.  The Profile Series UPS is a highly reliable, fully automatic on-line system.  All units feature full LED panel display with MTBF to over 250 khrs.  In the event of a complete power blackout, the UPS inverter continues to feed the computer system via the battery without any interruption to critical load.  This allows time to ride out the outage, switch to an auxiliary power source, or perform a controlled shutdown of the system without any danger to valuable data.

The use of Cell Saver Technology, an advanced battery management, charges the batteries only when necessary resulting in prolonged battery life, and up to 60 days advanced warning of pending battery service.  The 8-kVA to 12.5-kVA models offer convenient plug-in connection to the critical load with a wide range of individually protected receptacles on the optional power distribution module (PDM), which mounts on the rear of the unit.  The output may also be hardwired to a remote distribution panel.

In case of emergency, an Emergency Power Off (EPO) switch located on the unit which disconnects the critical load from both the UPS and the bypass. Remote Emergency Power-Off Stations (REPO) interface is also provided for remote power off.  The front panel offers an LED display of UPS conditions and a communications interface that allows transmission of UPS alarm conditions to a remote terminal. Models feature two RS232 ports for independent local and Network or modem communication. This communications interface also allows unattended automatic “soft” shutdown or event monitoring through the use of UPS monitoring software (see software section).

Profile models have a 2 year on-site service warranty and include system start-up (provided by vendor). Electrical installation must be by licensed electrician and may be contracted through an Environmental Products representative. Models are compatible with Power management software that ships with the AlphaServers. A cable kit or Network Adapter is required. Consult software section Powerware Profile Ordering Information – 8kVA- 12.5kVA Single Phase Models

Step 1—UPS Systems with Internal Battery

Select UPS system with internal battery; all models are 200-240V selectable output, hardwired input/output with optional plug-in output Power Distribution Module (PDM).

| 4N-AEAAK-DA | 8 kVA/5.6 kW, single-phase output (17 minutes at full load) – North American Model Only |
| --- | --- |
| 4N-AEAAL-DA | 10 kVA/7 kW, single-phase output (12 minutes at full load) – North American Model Only |
| 4N-AEAAM-DA | 12.5 kVA/8.75 kW, single-phase output (9 minutes at full load) – North American Model Only |

### Powerware Profile Office/Data Center Models (continued)

Step 2—Add-on Battery Cabinets

For support time beyond that included with above packaged systems.

| 4N-AEACK-AA | External Battery Cab EBC48 (half Cab) |
| --- | --- |
| 4N-AEACK-AB | External Battery Cab EBC96 (full Cab) |

Battery Runtimes in minutes

| Load | Load | UPS | ½ | 1 | 1½ | 2 | 2½ | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| (VA) | (W) | only | Cab | Cab | Cab | Cab | Cab | Cab | Cab | Cab | Cab | Cab | Cab | Cab | Cab |
| 2000 | 1400 | 80 | 195 | 329 | 477 | 636 | 805 |  |  |  |  |  |  |  |  |
| 3000 | 2100 | 52 | 127 | 215 | 311 | 415 | 525 |  |  |  |  |  |  |  |  |
| 4000 | 2800 | 37 | 92 | 156 | 226 | 301 | 381 | 464 | 642 |  |  |  |  |  |  |
| 5000 | 3500 | 29 | 71 | 120 | 175 | 233 | 295 | 359 | 497 |  |  |  |  |  |  |
| 6000 | 4200 | 23 | 58 | 97 | 141 | 188 | 238 | 290 | 401 | 520 | 645 | 775 | 911 | 1051 | 1196 |
| 7000 | 4900 | 19 | 48 | 81 | 117 | 156 | 198 | 241 | 334 | 433 | 536 | 645 | 758 | 875 | 996 |
| 8000 | 5600 | 17 | 41 | 69 | 100 | 133 | 168 | 206 | 284 | 368 | 457 | 550 | 646 | 745 | 848 |
| 9000 | 6300 | 14 | 35 | 60 | 86 | 115 | 146 | 178 | 246 | 319 | 396 | 476 | 560 | 646 | 735 |
| 10000 | 7000 | 13 | 31 | 52 | 76 | 101 | 128 | 157 | 217 | 281 | 328 | 419 | 492 | 568 | 647 |
| 11000 | 7700 | 12 | 28 | 47 | 68 | 90 | 114 | 139 | 193 | 250 | 310 | 373 | 438 | 506 | 575 |
| 12000 | 8400 | 11 | 25 | 42 | 61 | 81 | 103 | 125 | 173 | 224 | 278 | 335 | 393 | 454 | 517 |
| 12500 | 8750 | 9 | 23 | 40 | 58 | 77 | 97 | 119 | 165 | 213 | 265 | 318 | 374 | 431 | 491 |

Note:	Battery times are approximate and may vary with equipment, configuration, disk access, battery age, temperature, etc.

Step 3—Optional Plug-in Output Power Distribution Module (PDM)

Select one for 10 kVA and 12 kVA models

| 4N-AEACK-DA | (8) 5-15R2PDM W/8 5-15R2 |
| --- | --- |
| 4N-AEACK-DB | (2) L5-30R, (6) 5-15R2 |
| 4N-AEACK-DC | (6) L5-30R, (2) 5-15R2 |
| 4N-AEACK-DD | (2)L6-30R, (2) L6-20R, (2) L5-30R, (2) 5-15R2 |
| 4N-AEACK-DE | (2)L6-30R, (2) L5-20R, (2) L5-30R, (2) 5-15R2 |
| 4N-AEACK-DG | (2) 5-20R2, (2) L5-30R, (4) 5-15R2 |
| 4N-AEACK-DH | (2) 5-20R2, (3) L5-30R, (3) 5-15R2 |
| 4N-AEACK-DN | (3) L6-30R, (3) 5-20R2, (2) L5-20R |
| 4N-AEACK-DS | (1) L6-30R (2), L6-20R, (2) L5-20R, (3) 5-15R2 |
| 4N-AEACK-DT | (5) L6-30R, (1) L5-30R, (2) 5-15R2 |

### Powerware Profile Office/Data Center Models (continued)

Powerware Profile Single Phase Models Technical Specification

| Power Requirements |
| --- |
| Input Voltage | 200/100 V, 208/120 V, 220/110 V, 220/127 V, 240/120 V |
| Voltage Range | Single phase 85 V-146 V phase to Neutral; 170 V-292 V Line to Line |
| Input Frequency | 45/65 Hz |
| Power Factor | 0.95 |
| Efficiency | 89% (online) |
| Efficiency Optimizer | 98% |
| Input Connection | Hardwired |
| Input Breakers | 50A (8kVA model), 60A (10kVA model), 70A (12.5kVA model) |
| Output Voltage | 200/100 V, 208/120 V, 220/110 V, 220/127 V, 240/120 V |
| Output VA/Watts | 8000 VA/5600 W (8kVA model), 10000 VA/7000 W (10kVA model, 12500 VA/8750 W (12.5kVA model) |
| Output Frequency | 50 Hz/60 Hz |
| Output Breaker | 50A (8kVA model), 60A (10kVA model), 70A (12.5kVA model) |
| Voltage Distortion | < 2% THD (linear load), < 5% THD (nonlinear load) |
| Overload Capacity | 150% 30sec (on inverter), 1000% 20ms (on by-pass) |
| Battery-sealed lead acid Back-up time Recharge time | 17 minutes (8kVA model), 12 minutes (10kVA model), 9 minutes (12.5kVA model) < 5 hours up to 90% capacity |
| Physical Characteristics |
| Weight (with internal battery) | 556 lbs/208 kg |
| Dimensions (electronics or add-on battery) | 15.75 in x 29.5 in x 28 in (400mm x 750mm x 710mm) |
| Add-on battery weight | 468 lbs (half full cab) 765 lbs (full cab) |
| Environmental |
| Audible Noise | < 50 dBA at 3 feet |
| Temperature | 0 C to 40 C, recommended 15 C -25 C |
| Heat Dissipation | 2728 BTU/hr (8kVA model), 2950 BTU/hr (10kVA model), 3690 BTU/hr (12.5kVA model) |
| Humidity | 0 to 90% HR non-condensing |
| RFI Suppression | FCC Class A |
| Safety | UL 1778 ;CUL |

### Powerware Plus Office/Data Center Models

The Powerware Plus UPS systems are available in four Ratings.  Plus 15kVA, 18kVA, 24kVA and 36kVA models support both single-and three-phase applications.  Units are upgradable: 15kVA to 18kVA and 24kVA to 36kVA.

The employment of insulated gate bipolar transistor (IGBT) technology makes these UPS products the smallest and lightest in their class.  Combining the attributes of high switching speed and high current-carrying capability, IGBT technology provides the most efficient design and quietest operation available.  Its quiet, compact design and portable operation make it suitable for both office and computer room environments.  All models are voltage and frequency selectable for 
200V-240 V, 50 Hz or 60 Hz outputs and feature a wide input tolerance of up to 176 V-276 V without using battery.  This unique flexibility allows complete worldwide portability.  Three-phase models are also available for 480 V/380 V/220 V or 415 V/230 V applications.  It is the unit of choice for frequency conversion, phase shift applications or special seismic requirements and includes castors for ease of portability.

The Powerware PLUS UPS is a highly reliable, fully automatic on-line system.  All units feature full LCD panel display with MTBF to over 250 khrs.  In the event of a complete power blackout, the UPS inverter continues to feed the computer system via the battery without any interruption to critical load.  This allows time to ride out the outage, switch to an auxiliary power source, or perform a controlled shutdown of the system without any danger to valuable data.  A wide range of battery support times are available for all types of applications.  In addition to battery backup protection, its double conversion design ensures maximum isolation from the utility source and provides precision control of voltage and frequency during normal operation, while supporting 100% non-linear load without derating.

The 15kVA to 18kVA models offer convenient plug-in connection to the critical load with a wide range of individually protected receptacles on the optional power distribution module (PDM), which mounts on the rear of the battery cabinet. The 15kVA and 18kVA models may have up to two PDMs.  The output may also be hardwired.

The 24kVA and 36kVA models may be hardwired to a remote distribution panel or an optional auxiliary cabinet may be selected.  The optional auxiliary cabinet contains such features as wrap-around maintenance bypass, 30 pole distribution panel with provision for Square D bolt-on or plug-in circuit breakers, input harmonic current reduction filter and a variety of input/output transformer options.  Flexible cables with integrated circuit breaker and receptacle are also available for raised floor applications.

In case of emergency, an Emergency Power Off (EPO) switch located on the Personal Series-PLUS unit disconnects the critical load from both the UPS and the bypass.  Remote Emergency Power-Off Stations (REPO) interface is also provided for remote power off.

The full featured front panel offers a programmable visual menu driven display of UPS conditions and a communications interface that allows transmission of UPS alarm conditions to a remote terminal.  This communications interface also allows unattended automatic soft shutdown or event monitoring through the use of UPS monitoring software.  (See software section).

Powerware Plus models include 2 year on-site service including system start-up provided by vendor. The Electrical installation must be by licensed electrician and may be contracted through an Environmental Products representative.  Models are also compatible with power Management software that ships with AlphaServers.  Consult Software section.

Powerware Plus Series 15kVA and 18kVA Models

For Ordering Information on Powerware Plus Series 15kVA and 18kVA Models see steps 1 through 4.

For Ordering Information on Powerware Plus Series 24kVA and 36VA Models see steps 1a through 5a.

Step 1—UPS Systems with packaged battery

Select UPS system with packaged battery; all models are 200 V –240 V selectable output, hardwired input/output with optional plug output Power Distribution Module (PDM).

| 4N-AEAAN-BA | 15kVA/10kW, three-phase output, STD model (10 minutes at full load) |
| --- | --- |
| 4N-AEAAN-BC | 15kVA/10kW, three-phase output, EXT1 model (16 minutes at full load) |
| 4N-AEAAN-BD | 15kVA/10kW, three-phase output, EXT2 model (29 minutes at full load) |
| 4N-AEAAP-BA | 18kVA/12kW, three-phase output, STD models(7 minutes at full load) |
| 4N-AEAAP-BC | 18kVA/12kW, three-phase output, EXT1 models(12minutes at full load) |
| 4N-AEAAP-BD | 18kVA/12kW, three-phase output, EXT2 models(22 minutes at full load) |
| 4N-AEAAN-BE | 15kVA/10kW, three-phase output, International model with 380-415/220V output (10 minutes at full load) |

### Powerware Plus Office/Data Center Models (continued)

Step 2—Add-on Battery Cabinets

For support time beyond that included with above packaged systems.

| 4N-AEACH-BB | External Battery Cab for 15kVA and18kVA (EBC2) |
| --- | --- |

Battery Duration Table

Battery runtime chart full/half load support time in minutes.

| Models | kW | Standard Package with (1) EBC1 & (1) EBC2 | EXT 1 Package with (2) EBC2 | EXT 2 Package with (3) EBC2 | Add-on to EXT 2 Package with (1) EBC2 | Add-on to EXT 2 Package with (2) EBC2 |
| --- | --- | --- | --- | --- | --- | --- |
| 15kVA, three-phase | @ 10kW | 10/28 | 16/40 | 29/65 | 41/89 | 53/113 |
| 18kVA, three-phase | @ 12kW | 7/22 | 12/33 | 22/53 | 33/71 | 43/94 |

Step 3—Power Distribution Module (PDM) (Optional)

Select one or two for 15 kVA and 18 kVA models.

Use of two modules requires a conduit mount kit on one of the Power Distribution Modules.  Kit may also be used for combination hardwire/plug-in

Prestige extender PDM modules may be used for receptacle requirements beyond that shown.  Consult Prestige Series 3000/6000 section.  Select input plug to match twist loc receptacle on PDM.  L6-30, L6-20, or L14-30 recommended to balance 120V loads.

| 4N-AEACM-BA | (6) 5-20R2 |
| --- | --- |
| 4N-AEACM-BB | (4) 5-15R, (1) L21-20R |
| 4N-AEACM-BC | (4) 5-20R2, (2) L14-30R |
| 4N-AEACM-BD | (2) 5-15R2, (1) L5-30R, (1) L21-30R, (1) L21-20R |
| 4N-AEACM-BE | (1) 5-15R2, (3) L5-30R, (1) L21-20R |
| 4N-AEACM-BF | (5) 5-15R2, (1) L5-30R |
| 4N-AEACM-BG | (4) 5-15R2, (1) L21-30R |
| 4N-AEACM-BH | (3) 5-20R2 with conduit mount kit to add second PDM |
| 4N-AEACM-BJ | (1) 5-20R2, (1)L21-30R with conduit mount kit to add second PDM |
| 4N-AEACM-BK | (3) 5-20R2, (2) L21-30R |
| 4N-AEACM-BL | (1) 5-15R2, (3) 5-20R2, (1) L21-30R |
| 4N-AEACM-BM | (2) L5-20R, (2) 5-20R2, (1) L21-30R |
| 4N-AEACM-BN | (2) L21-30R, (1) 5-20R2, (2) L6-30R |
| 4N-AEACM-BP | (4) L5-30R, (1) L21-30R |
| 4N-AEACM-BS | (1) L6-30R, (2) L6-20R, (1) L21-30R, (1) 5-15R2 |
| 4N-AEACM-BT | (2) L21-30R with conduit mount kit to add second PDM |
| 4N-AEACM-PA | Package of (2) PDMs; 4N-AEACM-BT/BK (4) L21-30R, (3) 5-20R2 |
| 4N-AEACM-CA | (1) 5-15R, (2) L6-30R, (3) L5-30R |
| 4N-AEACM-CB | (2) 5-15R, (2) L6-20R, (3) L5-30R |
| 4N-AEACM-CC | (6) L5-30R |
| 4N-AEACM-CD | (1) 5-15R, (2) L5-30R , & Conduit mount kit to add second PDM |

### Powerware Plus Office/Data Center Models (continued)

Step 4—Software Communication, Network and Surge Protection Options

Power management & monitoring software included in AlphaServer shipments – Connect-UPS network adapter or multi interface kit required.  Ala Carte packages also available. Consult Software section for detail.  See Also UPS options and TVSS section. See also UPS Options and TVSS section.

Powerware Plus Office/Data Center Models Technical Specification

| Power Requirements | 15.0 kVA | 18.0 kVA |
| --- | --- | --- |
| Input Voltage | 176–253 V ac | 176–253 V ac |
| Phases | 3-phase | 3-phase |
| Frequency Range | 45–65 Hz | 45–65 Hz |
| Power connection | 95 typical | 95 typical |
| Input plug | Hard-wired | Hard-wired |
| Input circuit breaker | 60 amps, 3 pole only | 60 amps, 3 pole only |
| Maximum input current | 42 A | 50 A |
| kVA/kW | 15.0/10.0 | 18.0/12.0 |
| Output Voltages (selectable) | 100/200, 127/220, 120/208 (North America Models) 220/380, 230/400, 240/415 (International Models) | 100/200, 127/220, 120/208 (North America Models) 220/380, 230/400, 240/415 (International Models) |
| Maximum current continuous | 42 A | 50 A |
| Sustained overload before bypass transfer | 106 to 125% FLA @ 10 minutes; 126 to 149% @ 30 seconds; >150% @ 10 cycles | 106 to 125% FLA @ 10 minutes; 126 to 149% @ 30 seconds; >150% @ 10 cycles |
| Fault clearing | 150 A @ 10 cycles; >150 A @ 3 milliseconds | 150 A @ 10 cycles; >150 A @ 3 milliseconds |
| Transient response | <5% for 100% load Step within 1 millisecond; full recovery within 1 cycle | <5% for 100% load Step within 1 millisecond; full recovery within 1 cycle |
| Voltage regulation | <+-2% | <+-2% |
| THD | <5% for full nonlinear loads and 3.0 crest factor | <5% for full nonlinear loads and 3.0 crest factor |
| Frequency regulation | 50 or 60 Hz +-0.1% (free run) | 50 or 60 Hz +-0.1% (free run) |
| Battery-sealed lead acid/5year design life DC voltage Approvals | 240 V dc; 120 cells, 2.25 V/cell float IATA Special Provision 67, U.S. DOT, and IMDG test standards | 240 V dc; 120 cells, 2.25 V/cell float IATA Special Provision 67, U.S. DOT, and IMDG test standards |
| Physical Characteristics |
| Weight2 UPS & Packaged Battery Standard Models UPS Cabinet Only Each Battery | 655 lb (298 kg)/780 lb shipping 180 lb (82 kg)/235 lb shipping (EBC1) 171 lb (76 kg)/205 lb shipping (EBC2) 295lb (134kg)/340 lb shipping | 655 lb (298 kg)/780 lb shipping 180 lb (82 kg)/235 lb shipping (EBC1) 171 lb (76 kg)/205 lb shipping (EBC2) 295lb (134kg)/340 lb shipping) |
| Dimensions1,2 UPS & Packaged Battery Standard Models UPS Cabinet Only Each Battery | 28.1 x 25.5 x 28.6 in./(714 x 648 x 625 mm) 28.1 x 8.5 x 28.6 in 28.1 x 8.5 x 24.6 in (7.4 x 216 x 625 mm) | 28.1 x 25.5 x 28.6 in./(714 x 648 x 625 mm) 28.1 x 8.5 x 28.6 in 28.1 x 8.5 x 24.6 in (7.4 x 216 x 625 mm) |

### Powerware Plus Office/Data Center Models (continued)

| Environmental |
| --- |
| Audible Noise | Typically <50 dBA at 1 meter | <60 dBA at 1 meter |
| Audible Noise | Typically <50 dBA at 1 meter | <60 dBA at 1 meter |
| Ambient Temperature | 0° C to +40° C | 0° C to +40° C |
| Relative humidity | 5%–95% noncondensing | 5%–95% noncondensing |
| Surge/electrostatic (ESD) | Meets IEEE 587/ANSI C62.41 Class A, B; 25 kV withstand for ESD | Meets IEEE 587/ANSI C62.41 Class A, B; 25 kV withstand for ESD |
| EMI suppression | Meets FCC Part 15, Subpart J, Class A | Meets FCC Part 15, Subpart J, Class A |
| Safety | IEC 950, UL 1778, Canadian Standards Association listed | IEC 950, UL 1778, Canadian Standards Association listed |

1.	Service clearance required=4-in rear, 36-in left facing unit, PDM adds 4-in to depth of battery cabinets.

2.	Add an additional 8.5-inches to width for international 15kVA or 18kVA model. Call for weight information on these models.

Powerware PLUS Series—PUPS-Plus (24 and 36kVA Models)

Step 1a—UPS with packaged battery

| 4N-AEAAR-AA | 24 kVA, one battery cabinet, 12 minutes |
| --- | --- |
| 4N-AEAAR-AB | 24 kVA, two battery cabinets, 30 minutes |
| 4N-AEAAR-AC | 24 kVA, three battery cabinets, 50 minutes |
| 4N-AEAAS-AA | 36 kVA, one battery cabinet, 12 minutes |
| 4N-AEAAS-AB | 36 kVA, two battery cabinets, 30 minutes |
| 4N-AEAAS-AC | 36 kVA, three battery cabinets, 50 minutes |

Step 2a—Additional Auxiliary Options Cabinet with Input/Output Options (Optional)

All cabinets contain external wraparound bypass. Power Distribution Modules (PDMs) include space for 30 single pole circuit breakers and accepts Square D plug-in, or bolt-on circuit breakers.

Note:	Option cabinets cannot be ordered as a field upgrade.

With Step Down Transformer

| 4N-AEACP-AC | Auxiliary cabinet, 480 input/200-220V output |
| --- | --- |
| 4N-AEACP-AD | Auxiliary cabinet, 480 input/200-220V output with PDM (30-pole) |
| 4N-AEACP-AE | Auxiliary cabinet, 480 input/480 output |
| 4N-AEACP-BC | Auxiliary cabinet, 480 input/200-220V output with THD inputfilter |
| 4N-AEACP-BD | Auxiliary cabinet, 480 input/200-220V output with PDM (30-pole) and THD input filter |
| 4N-AEACP-BE | Auxiliary cabinet, 480 input/480 output with THD input filter |

Without Step Down Transformer

| 4N-AEACP-AA | Auxiliary cabinet with ext bypass only |
| --- | --- |
| 4N-AEACP-AB | Auxiliary cabinet with PDM (30-pole) |
| 4N-AEACP-BA | Auxiliary cabinet with THD input filter |
| 4N-AEACP-BB | Auxiliary cabinet with PDM (30-pole) and THD input filter |

### Powerware Plus Office/Data Center Models (continued)

Step 3a—Distribution Cables (Optional)

Cable required if PDM is selected in Step 2.

Cables can be ordered at 20 feet, 30 feet or 40 feet in length.

Includes Square D plug-in circuit breaker and receptacles shown below (bolt-on breaker available, call for information).

For hardwire output to remote distribution applications see optional Modular Power Distribution Units section.

| 4N-BC24K-xx | (2) 5-15R with 15A-1P circuit breaker |
| --- | --- |
| 4N-BC24L-xx | (4) 5-15R with 15A-1P circuit breaker |
| 4N-BC24N-xx | (2) 5-20R with 20A-1P circuit breaker |
| 4N-BC24P-xx | (4) 5-20R with 20A-1P circuit breaker |
| 4N-BC24S-xx | (1) L5-30R with 30A-1P circuit breaker |
| 4N-BC24T-xx | (1) L6-20R with 20A-2P circuit breaker |
| 4N-BC24U-xx | (1) L14-20R with 20A-2P circuit breaker |
| 4N-BC24V-xx | (1) L21-20R with 20A-3P circuit breaker |
| 4N-BC24W-xx | (1) L21-30R with 30A-3P circuit breaker |
| 4N-BC26E-xx | (1) L6-30R with 30A-2P circuit breaker |
| 4N-BC28Z-xx | (1) L14-30R with 30A-2P circuit breaker |

Step 4a—Software and Other Options

See software section and order chart for applicable operating system.  See UPS Hardware options for network adapters.  See TVSS section for surge protection.

Step 5a—Add-on Battery Field Upgrades

Add-on battery for increased support time.

Maximum of three total including package battery recommended to limit recharge time.

| 4N-AEACN-AA | Add-on matching battery cabinet |
| --- | --- |

Powerware PLUS Series—PUPS-Plus (24 and 36kVA Models) Technical Specification

Note:	Service clearance required = 4 inches rear, 36 inches left side facing unit.

| Models | 24 kVA1 | 36 kVA |
| --- | --- | --- |
| Input |
| Nominal voltage VAC | 208 V | 480 V | 208 V | 480 V |
| Input voltage range | 176-253 V | 410-580 V | 176-253 V | 410-580 V |
| Phases | 3-phase |
| Frequencies | 45—65 Hz |
| Power factor | 95 typical |
| Input connection | Hardwire at rear of unit |
| Input circuit breaker 3-pole | 125A-3P | 75A-3P | 125A-3P | 75A-3P |
| Maximum input current | 58A | 28A | 87A | 42A |
| Input current THD | Less than 10% with optional THD reduction filter |

### Powerware Plus Office/Data Center Models (continued)

| Output |
| --- |
| kVA/kW | 24/16 | 36/24 |
| Voltages (selectable) | 115/200, 120/208, 127/220 VAC/480/277 VAC with options cabinet |
| Phases | 3-phase |
| Continuous Amps | 67A | 29A | 100A | 44A |
| Sustained overload before bypass transfer | 106% to 125% FLA @ 10 minutes, 126% to 149%@ 30 seconds, >150%, 10 cycles |
| Fault clearing | 300 A @ 12 cycles, >300 A, 3 ms |
| Transient response | <5% for 100% load Step, recovery in ¼ cycle (4 ms) |
| Voltage regulation | < ±2% |
| THD | <5% maximum for full non-linear and 100% load |
| Frequency regulation | 50 or 60 Hz ±0.1% (free run) |
| Noise attenuation to 100kHz | Common/Normal mode >100/60 dB |
| Agency Compliance |
| Surge/electrostatic (ESD) | Meets IEEE 587/ANSI C62.41 Class A, B; 25 kV withstand for ESD |
| EMT suppression | Meets FCC Part 15, Subpart J, Class A |
| Safety | IEC 950, UL 1778, Canadian Standards Association listed |
| Batteries Information |
| Manufacturer/type/life | YUASA, NP series/sealed, maintenance-free lead acid/5-year design life |
| Approvals | Meets IATA Special Provision 67, U.S. DOT, and IMDG test standards |
| DC voltage | 240 Vdc; 120 cells, 2.25 V/cell float |
| Recharge times to 90% | 1 cabinet, 1 hour, 2 cabinets 2 hours, 3 cabinets 3 hours |
| Battery Times Full/Half Loads in Minutes2 | 24kVA Models @ 16kW 36kVA Models @ 24 kW | With 1 cabinet 12/30 5/18 | with 2 cabinets 30/80 15/30 | with 3 cabinets 50/130 30/80 |
| Environmental and Physical |
| Size (same for electronics, or auxiliary or battery cabinet)4 | 39 in. H x 17 in. W x 31 in. D (each cabinet)3 |
| System weights |  |
| Electronics module Auxiliary cabinet | UPS: 400 lb (180 kg) 1300 lb (590 kg) maximum with all options |
| Battery weight | 900 lb per cabinet |
| Altitude | 5000 ft (1500 m) above sea level |
| Audible noise @ 1 meter | 65 dBA |
| Ambient temperature |
| Operating | 0° to +40° C |
| Nonoperating | –20° to 60° C |
| Relative humidity | 5% to 95% noncondensing |
| Btus/hour | 10,402 (24 kVA), 15,602 (36 kVA) |

1.	24 kVA unit is field upgradable to 36 kVA

2.	Additional support time available, call for information

3.	Service clearance required is 4 inches rear, 36 inches left side facing unit

4.	Add 6.2 inches to depth of electronics, and auxiliary cabinet for wiring trough

### Standby UPS Systems

Positioned for low end standalone and client PCs which require a minimum of power conditioning and basic blackout protection, Standby UPS systems offer a base level of filtering/surge protection during normal operation and battery back-up with safe shutdown provisions during a power failure. They generally engage in 4-8ms and operate on battery during power outage, or brownout/overvoltage conditions. They are the cost effective choice to ensure data integrity for clients in a PC client-server environment. Compaq offers solutions from Exide Electronics (One-UPS Plus).

| One-UPS (300-650VA) |
| --- |
| Battery Start | Yes (420,650) |
| Adjustable Brownout Transfer Settings | Yes |
| Basic Monitoring Port | Yes |
| Site Wiring Fault Indicator | Yes |
| On Battery/On Utility LED | Yes (420, 650VA) |
| Audible Alarms | Yes |
| 50/60Hz selectable | Yes |
| User replaceable battery | No |
| Warranty | 3 year advance exchange |

One-UPS Plus Models Ordering Information

| 120V/230V Models |  | Capacity VA/Watts | Battery (min) | Receptacle No. 120V/230V2 |
| --- | --- | --- | --- | --- |
| 4N-AEADA-AF/BF | One-UPS Plus 300VA | 300VA/180W | 9 minutes full load | (2) 5-15/2 IEC320 |
| 4N-AEADA-AG/BG | One-UPS Plus 420VA | 420VA/250W | 6 minutes full load | (2) 5-15/2 IEC320 |
| 4N-AEADA-AH/BH | One-UPS Plus 650VA | 650VA/400W | 5 minutes full load | (4) 5-15/4 IEC320 |

One-UPS Plus Specifications

| One-UPS Plus Models | Weight/Net Shipping | H x W x D (inches) |
| --- | --- | --- |
| 300VA | 11 lbs | 6.0 x 3.4 x 13.5 |
| 420VA | 11 lbs | 6.0 x 3.4 x 13.5 |
| 650VA | 25 lbs | 6.6 x 4.7 x 14.2 |

### UPS Options

Options for Prestige Desktop/Office Models

Note:	-PA models include (7) 5-15R outlets “on” UPS and (1) 5-15R “off” UPS for laser printer.
-PB models include (6) IEC 10A “on” UPS and (1) IEC 10A “off” UPS.  All outlets have built-in surge protection.

| 4N-AEAEO-PA | Hot Swap PowerPass (120V) | Allows safe swap out of UPS without affecting load (up to 1800VA models) |
| --- | --- | --- |
| 4N-AEAEO-PB | Hot Swap PowerPass (230V) | Allows safe swap out of UPS without affecting load (up to 1800VA models) |
| 4N-AEAEO-RA | Rackmount kit (22-27"D) | Includes single (9.25" high) and double (12.1" high) unit faceplate, 19” width up to 2000VA models. 22-27-inch adjustable depth |
| 4N-AEAEO-RB | Rackmount kit (28-32"D) | Includes single (9.25" high) and double (12.1" high) unit faceplate, 19” width up to 2000VA models, 28-32 inches adjustable depth |
| 4N-AEAEO-RC | Rackmount kit (25"D) | Includes 1-3 unit faceplate in 6U High (10.5") assembly, 19” width for Prestige 3000, may be used for multiple desktop units |
| 4N-AEACH-Hx | Mobile Stacker Unit | Includes seismic mounting provisions for Prestige Models 3000 and 6000 x = A/B/C/D for 3, 4, 5, or 6 high module configuration (5.6” each) See Prestige 3000/6000 Section for configuration details. |

### UPS Options (continued)

Network Adapters for Prestige and Powerware Plus & Profile Models

Connect-UPS SL preferable for connection to Profie Models.

Note:	PUPS Plus 24 and 36kVA models require 4 ft connector cable, call for information.

| 4N-AEAEO-DA/DC | Connect-UPS Ethernet (120V) | Ethernet/SNMP Adapter: DA= twisted-pair 10BaseT/DC= ThinWire |
| --- | --- | --- |
| 4N-AEAEO-DB/DD | Connect-UPS Ethernet (240V- IEC) | Ethernet/SNMP Adapter; DB= twisted-pair 10BaseT/DD= ThinWire |
| 4N-AEAEO-CJ/CK | Connect-UPS Token Ring | SNMP Thinwire and twisted-pair CJ= 120V; CK= 240V |
| 4N-AEAEO-DE/DF | Connect-UPS SL | SNMP Adapter DE= Twisted pair 10BaseT; DF= Token Ring |

Upgrade Kits for PUPS Plus

Not customer installable, requires service engineer.

| 4N-AEAAL-CA | 10 to 12kVA |
| --- | --- |
| 4N-AEAAN-CA | 15 to 18kVA |

### Modular Power Distribution/Conditioning Systems

These power distribution modules and conditioning distribution modules are designed to be the central source of distribution and conditioning of electrical power to computer equipment. They replace the H7317 (PDS+) and H7318 (PCS+) product set.  Combined with flexible output distribution cables, these systems offer maximum flexibility and portability to preserve capital investment and lower lifecycle costs.

Features

Microprocessor monitoring and isolation.

Optional environmental monitoring package.

LCD display of many different power parameters

Audible/visual alarms.

Emergency power-off circuit.

Shielded isolation transformer for electrical noise reduction.

Output distribution panels with 42 pole positions at 30 kVA and 84 poles at all other levels, up to 100 kVA.

Completely compatible with the present “BC” series of flexible power distribution cables; offer a portable and reliable equipment connection and come pre-assembled with circuit breakers and receptacles.

Conditioning distribution module provides electronic voltage regulation with auto-bypass control, in case of regulator failure; can accept input voltage range from –27% to +15% while maintaining an output voltage of ±3% of nominal.

Ideal for facilitating computer room consolidations.

Configuration Information

Determine NEMA plug type and select cables with breakers and receptacles.

Note the number of poles required to select appropriate PDM or CDM. Specify Square D or Bryant type circuit breakers.  See PDM/CDM distribution cable chart

Models without monitoring are also available.

All Power Distribution Models and Conditioning Distribution Modules are 3 phase, 208/120V output

Power Distribution Modules (PDM) 208V Input Models

| 4N-CUPDM-AB | 30-kVA PDM, 42 poles, |
| --- | --- |
| 4N-CUPDM-AJ | 50-kVA PDM, 84 poles |
| 4N-CUPDM-AD | 75-kVA PDM, 84 poles |
| 4N-CUPDM-AE | 100-kVA PDM, 84 poles |

Power Distribution Modules (PDM) 480V Input Models

| 4N-CUPDM-HB | 30-kVA PDM, 42 poles |
| --- | --- |
| 4N-CUPDM-HJ | 50-kVA PDM, 84 poles |
| 4N-CUPDM-HD | 75-kVA PDM, 84 poles |
| 4N-CUPDM-HE | 100-kVA PDM, 84 poles |

### Modular Power Distribution/Conditioning Systems (continued)

Conditioning Distribution Modules (CDM) 208V Input Models

| 4N-CUCDM-AB | 30-kVA CDM, 42 poles |
| --- | --- |
| 4N-CUCDM-AJ | 50-kVA CDM, 84 poles |
| 4N-CUCDM-AD | 75-kVA CDM, 84 poles |
| 4N-CUCDM-AE | 100-kVA CDM, 84 poles |

Conditioning Distribution Modules (CDM) 480V Input Models

| 4N-CUCDM-HB | 30-kVA CDM, 42 poles |
| --- | --- |
| 4N-CUCDM-HJ | 50-kVA CDM, 84 poles |
| 4N-CUCDM-HD | 75-kVA CDM, 84 poles |
| 4N-CUCDM-HE | 100-kVA CDM, 84 poles |

PDM/CDM distribution cable chart

Includes square D plug-in circuit breaker and receptacles shown.  Suffix denotes length in feet.

| 4N-BC24K-20/30/40 | (2) 5-15R with 15A-1P circuit breaker |
| --- | --- |
| 4N-BC24L-20/30/40 | (4) 5-15R with 15A-1P circuit breaker |
| 4N-BC24N-20/30/40 | (2) 5-20R with 20A-1P circuit breaker |
| 4N-BC24P-20/30/40 | (4) 5-20R with 20A-1P circuit breaker |
| 4N-BC24S-20/30/40 | (1) L5-30R with 30A-1P circuit breaker |
| 4N-BC24T-20/30/40 | (1) L6-20R with 20A-2P circuit breaker |
| 4N-BC24U-20/30/40 | (1) L14-20R with 20A-2P circuit breaker |
| 4N-BC24V-20/30/40 | (1) L21-20R with 20A-3P circuit breaker |
| 4N-BC24W-20/30/40 | (1) L21-30R with 30A-3P circuit breaker |
| 4N-BC26E-20/30/40 | (1) L6-30R with 30A-2P circuit breaker |
| 4N-BC28Z-20/30/40 | (1) L14-30R with 30A-2P circuit breaker |

Specifications for PDM, CDM, and PDU (PDM and CDM with Monitoring)

| kVA | H x W x D | Unit Weight (PDM) | Unit Weight (CDM) |
| --- | --- | --- | --- |
| 30 | 62 x 27 x 27 inches (157 x 68 x 68 cm) | 540 lb (245 kg) | 1160 lb (527 kg) |
| 50 | 69 x 34 x 34 inches (175 x 86 x 86 cm) | 795 lb (361 kg) | 1675 lb (761 kg) |
| 75 | 69 x 34 x 34 inches (175 x 86 x 86 cm) | 935 lb (426 kg) | 1975 lb (898 kg) |
| 100 | 69 x 34 x 34 inches (175 x 86 x 86 cm) | 1055 lb (480 kg) | 2360 lb (1073 kg) |

### Transient Voltage Surge Suppressers

The 4N-GAXXX family of Transient Voltage Surge Suppresser (TVSS) products prevent high-energy impulses that can damage a computer system or corrupt data. ZoneGuardian, ZoneMaster, and ZoneSentinel devices include user-friendly LED diagnostics to indicate faulty wiring and operational readiness.

ZoneMaster power panel devices include redundant parallel modules and auxiliary contacts for remote annunciation. Flexible “plug and play'' power strip and snap-in data communication modules ensure total desktop protection. All devices carry a full 5-year warranty.

Zone Guardian power/data system includes connected load hardware warranty. Zone Guardian Plus power/data system includes additional 1 year software and stored data operational warranty.

### Transient Voltage Surge Suppressers

TVSS Quick Selection Chart

Note:	All power protector models feature protection on all modes (L-N, L-G, and N-G) at 330V maximum let through voltage.

| AC Power Surge Devices | Order Number | Application | Configuration | Maximum Surge | Peak clamp1 (Voltage maximum) |
| --- | --- | --- | --- | --- | --- |
| ZoneGuardian | 4N-GA353-xx2 | Terminals, PCs, desktop UPS systems, fax machines, client workstations, printers | (7)5-15R | 10 kA | 400V (L-N)3 330V (L-N)4 |
| ZoneGuardian Plus | 4N-GA420/430-xx | High-end workstations, servers | 3 and 7 5-15R | 10 kA | 270V (L-N)3 240 V (L-N)4 |
| ZoneMaster 140 | 4N-GA171-xx | Primary power panel | 1 per panel | 300 kA | 400–1500V3 |
| ZoneMaster 75 | 4N-GA112-xx | Primary or secondary power panel | 1 per panel | 150 kA | 400–800V3 |
| ZoneSentinel7 | 4N-GA121-xx | Secondary power panel7 | 1 per panel | 40 kA | 400–1000V3,8 |
| ZoneGuardian CPP | 4N-GA240-xx5 | Snap-in extender modules for Desktop data/tel | Up to 4 per Zone Guardian or SCP module | 2 kA | 10–27V(data)6 105–270 (tel) |
| SCP Series | 4N-GA249-xx | Used with UPS system for total protection | Plugs into standard 15A receptacle, add up to 4 CPP modules per receptacle |  | 10–27V (data)6 105–270 (tel) |
| Zone Barrier Series | 4N-GA245-xx | Standalone & Din rail mount | Up to 32 modules per rail, rack or wall mount |  | 12-27V (data) |
| MDL Series Enclosure Modules Cables | 4N-GA250-xx 4N-GA262-xx 4N-GA264-xx 4N-GA270-xx 4N-GA272-xx 4N-GA276-xx 4N-GA277-xx | Data Truck Line | 3 & 20 modules per enclosure | 1.9-3 kA | 12-27V (data)6 105-270V (tel) |

1.	Minimum Clamp V threshold of power modules is 150.

2.	Use 4N-GA440-AD for systems with 5-20R plug.

3.	Clamp V at 6 kV (1.2/50 ms) and 3 kA (8/20 ms) IEEE CAT B impulse test. UL 1449 for panel devices.

4.	Clamp V at 6 kV (1.2/50 ms) and 500A (8/20 ms) UL 1449 for receptacle devices.

5.	4N-GA240 data protection modules must be used in combination with 4N-GA350/420/430  & 4N-249 plug surge protectors. Number of modules unlimited on strip models.

6.	Clamp V at 2 kV (1.2/50 ms) and 1000A (8/20 ms).

7.	Also for any system requiring 3-phase power or non-standard plug types.

8.	When used in series with Zonemaster devices, maximum let through voltage is 330V.

### Transient Voltage Surge Suppressers (continued)

Application Information

Panelboard Protection

- Main panel protection is the single best way to reduce all high-level power surges from external disturbances to safe levels within the building.

- Use the ZoneMaster 75 series at the service entrance of small single three-story facilities and at sub-panels feeding sensitive equipment. Use the 140 series at the service entrance of larger facilities or where lightning is more prevalent, such as the southeastern and southern areas of the U.S.

- Zone Sentinel devices are ideal for protecting a dedicated secondary panel within a building or may be used as main panel protection to handle lower surge levels.

Desktop Power and Data/Network Protection

- As long as there is a communications port available on the device to be protected, it is important that BOTH power AND the communications port are protected. Protecting power or data/telephone alone in these situations increases the likelihood of voltage potential differences and resulting damage to equipment.

AC Desktop Protector Options

ZoneGuardian Plus—Premium Performance (10 KA max)

| 4N-GA420-AD | Three-outlet, 15A wall plug |
| --- | --- |
| 4N-GA430-AF | Three-outlet, 15A power strip2 |
| 4N-GA430-AG | Seven-outlet, 15A power strip2 |
| 4N-GA440-AD1 | One 20A 5-20R outlet with wall plug2 |
| 4N-GA440-AE1 | One 20A L5-20R outlet with wall plug2 |

ZoneGuardian—High Quality Performance (10 KA max)

| 4N-GA353-BC | Seven-outlet, 15A power strip |
| --- | --- |
| 4N-GA353-BD | Seven -outlet, 15A power strip with Tel Surge protection |

1.	Not ZoneGuardian Series Devices—will not accept CPP modules.

2.	All Power Strips and GA440 devices furnished with 6-foot cord.

AC Panel Protection ZoneMaster 140—Main Panel Protection (140 KA max)

| 4N-GA171-AA | 120/240V 1-phase 3W, 400V clamp |
| --- | --- |
| 4N-GA171-AB | 120/208V 3-phase 4W WYE, 400V clamp |
| 4N-GA171-AC | 120/240V 3-phase 4W Delta, 400V clamp |
| 4N-GA171-AD | 240V 3-phase 3W Delta, 800V clamp |
| 4N-GA171-AE | 277/480V 3-phase 4W WYE, 800V clamp |
| 4N-GA171-AG | 480V 3-phase 3W Delta, 1500V clamp |

ZoneMaster 75—Main and Secondary Panel Protection (75 KA max)

| 4N-GA112-AA | 120/240V 1-phase 3W, 400 V clamp |
| --- | --- |
| 4N-GA112-AB | 120/208V 3-phase 4W WYE, 400 V clamp |
| 4N-GA112-AC | 120/240V 3-phase 4W Delta, 400 V clamp |
| 4N-GA112-AD | 240 V 3-phase 3W Delta, 800 V clamp |
| 4N-GA112-AE | 277/480V 3-phase 4W WYE, 800 V clamp |
| 4N-GA112-AG | 480V 3-phase 3W Delta, 1500 V clamp |

### Transient Voltage Surge Suppressers (continued)

ZoneSentinel—Secondary Panel Protection (40 KA max)

| 4N-GA121-AA | 120/240V 1-phase 3W, 400 V clamp |
| --- | --- |
| 4N-GA121-AB | 120/208V 3-phase 4W WYE, 400 V clamp |
| 4N-GA121-AC | 120/240V 3-phase 4W Delta, 400 V clamp |
| 4N-GA121-AD | 240V 3-phase 3W Delta, 600 V clamp |
| 4N-GA121-AE | 277/480V 3-phase 4W WYE, 1000 V clamp |

Communication Port Protection

ZoneGuardian Series CPP modules are supplemental snap-on devices to be used for communications port protection with ZoneGuardian AC surge or to extend the number of ports on SCP modules below.  Wall plug models limited to four modules per suppresser.

CPP Modules

| 4N-GA240-AB | 2 wire dial-up, RJ11 |
| --- | --- |
| 4N-GA240-AC | 2-2 wire dial-up, RJ11 |
| 4N-GA240-AD | 4 wire leased line, RJ11 |
| 4N-GA240-AE | 4 wire leased line, term strip |
| 4N-GA240-AF | 4 wire digital data, RJ485 |
| 4N-GA240-AG | 4 wire data, term strip |
| 4N-GA240-AH | 4 wire T1 RJ48C |
| 4N-GA240-AJ | 4 wire T1 term strip |
| 4N-GA240-AK | EIA-232 4 wire+SH, term strip |
| 4N-GA240-BA | EIA-232 5 wire, term strip |
| 4N-GA240-BB | EIA-232 8 wire, RJ45 |
| 4N-GA240-BC | EIA-232 6 wire, MMJ |
| 4N-GA240-BF | EIA-232 6 wire RJ45 |
| 4N-GA240-BG | EIA-423 4 wire+SH, term strip |
| 4N-GA240-BH | EIA-423 6 wire, MMJ |
| 4N-GA240-BJ | EIA-485 2 wire+GRD term strip |
| 4N-GA240-CB | IBM 3270 video one-wire with shield, BNC |
| 4N-GA240-EA | 8 wire UL category 5, RJ45 |

SCP Modules (standalone Communications Port Protectors)

Add up to 4 CPP modules to increase number of ports.

| 4N-GA249-BB | EIA-232 8 wire RJ45 |
| --- | --- |
| 4N-GA249-BH | EIA-232 6 wire RJ45 |
| 4N-GA249-AB | 2 wire Dial-Up, RJ11 Telco |
| 4N-GA249-AD | 4 wire leased line, RJ11 Telco |
| 4N-GA249-AF | 4 wire Digital Data, RJ48S Telco |
| 4N-GA249-BB | 8 wire RS232, RJ45 |
| 4N-GA249-BH | 6 wire RS423, MMJ |
| 4N-GA249-CA | 4 wire 10BaseT, RJ45 |

In-line Devices (attach to Device Port)

| 4N-GA700-BH | EIA-232, 12 wire, DB25F/DB25M |
| --- | --- |
| 4N-GA700-BA | EIA-232, 8 wire, DB9 |

Note:	All order numbers include one 7-foot data cable with mating connectors. CPP modules must be used with ZoneGuardian series AC TVSS devices. SCP modules plug into wall receptacle for standalone protection.

### Transient Voltage Surge Suppressers (continued)

Accessories for DB25 and DB9 EIA-232 Communication Interfaces

| H8575-A | MMJ-to-DB25 EIA-232 adapter |
| --- | --- |
| H8571-J | MMJ-to-DB9 EIA-232 adapter |
| BC16E-10 | 10-foot 6-wire jumper cable with MMJ connectors |

Note:	Use of these adapters will not allow full modem control.

Zone Barrier Din Rail Mount Devices

| 4N-GA245-AA | 17.5” Din Rail w/19” rackmount kit, up to 32 modules |
| --- | --- |
| 4N-GA245-AB | 2 wire Dial-Up, RJ11 |
| 4N-GA245-AC | 4 wire leased line, RJ11 |
| 4N-GA245-AF | 4 wire Digital Data Service, RJ48S Telco |
| 4N-GA245-AH | 4 wire TI, RJ48C Telco |
| 4N-GA245-BB | 8 wire RS232, RJ45 |
| 4N-GA245-CB | Coax IBM 3270/Video, RJ45 |
| 4N-GA245-CD | TwinAx IBM AS400/S3X |
| 4N-GA245-CF | 4 wire Dial-Up, RJ11 |
| 4N-GA245-CH | 4 wire Token Ring, RJ45 |
| 4N-GA245-EA | 8 wire RJ45, UL Category 5 |

Transient Voltage Surge Suppressers Specifications

| Technical Data | General/Environmental |
| --- | --- |
| Operating temperature range | –40° to 85° C (–40° to 185° F) |
| Operating humidity range | 0 to 95% (non-condensing) |
| Maximum continuous operating volts | 25% above nominal service voltage |
| Safety cutout | Thermal protection against sustained overvoltages above maximum continuous but below clamp level |
| Enclosures | Durable lightweight plastic UL94-5V flame retardant. ZoneMaster products meet NEMA 1, 2, 3R, 3S, 12, and 13 classifications |
| Three-function LEDs on power module | red = gnd not present or L-N reversal; green = normal operation Note: communication protector modules failsafe via short circuit to gnd. |
| Maximum Peak clamp volts1 | See TVSS (Quick Selection Chart) |

1.	Clamp levels given for L-N and L-L modes, where most damage occurs.

|  | ZoneGuardian 4N-GA350 | ZoneGuardian Plus 4N-GA420, 4N-GA430 |
| --- | --- | --- |
| Hybrid clamp circuit (MOV, coil, capacitor) | 3 stage | 5 stage |
|  | ZoneMaster 75 | ZoneMaster 140 | ZoneSentinel |
| Weight | 6 lb (2.72 kg) | 10 lb (4.54 kg) | 4 lb (1.8 kg) |
| Size | 10 x 8 x 4 in. | 12 x 12 x 6 in. | 8 x 6 x 4 in. |
| Stage/clamp component | Single stage MOV | Single stage MOV | Single stage MOV |
| No. redundant components | 2 @40 kA | 4@40 kA | 1@40 kA |
| Required input circuit breaker |  | 60 Amps | 30 Amps |